## Informationen
|  | Line |  | Trafo |  | Trafo Berechnung |  |  | Allgemin | [6 empty] | Kabel Berechnung
Core Nr. | Nr. | Ikmax | Itmax | Irt | Itf | TMVA | Un | Zt | Ipr | Isr | ALF | Rl | Rct | Sr | Sn | cabel length | cable diameter | max Temperatur
1 | 1 | 50 | 50 | 0.5 | 2 | 220 | 220 | 23 | 800 | 1 | 20 | 0.47886 | 7 | 0.02 | 30 | 90 | 4 | 75
1 | 4 | 6.6 | 50 | 1.2 | 6.6 | 310 | 150 | 18 | 1250 | 1 | 20 | 0.34584 | 7 | 0.02 | 10 | 65 | 4 | 75
2 | 5 | 29 | 40 | 1.25 | 29 | 325 | 150 | 5 | 1250 | 1 | 20 | 0.34584 | 7 | 0.02 | 10 | 65 | 4 | 75
3 | 7 | 40 | 40 | 1.193 | 8 | 310 | 150 | 18 | 1250 | 1 | 20 | 0.39905 | 7.5 | 0.02 | 30 | 75 | 4 | 75
4 | 10 | 40 | 40 | 0.8 | 6 | 200 | 150 | 15 | 1600 | 1 | 40 | 0.37245 | 7.5 | 0.02 | 10 | 70 | 4 | 75
1 | 2 | 31.5 | 31.5 | 2 | 16 | 110 | 33 | 12 | 2500 | 1 | 20 | 0.18445 | 14 | 0.02 | 15 | 13 | 1.5 | 75
2 | 3 | 40 | 40 | 2.7 | 29 | 175 | 33 | 12 | 3000 | 1 | 60 | 0.58527 | 20 | 0.02 | 30 | 110 | 4 | 75
3 | 6 | 29 | 30 | 2.7 | 25 | 155 | 33 | 12 | 2500 | 1 | 20 | 0.29264 | 14 | 0.02 | 20 | 55 | 4 | 75
4 | 8 | 29 | 29 | 2.712 | 25 | 155 | 33 | 10 | 3000 | 1 | 20 | 0.42565 | 18 | 0.02 | 20 | 80 | 4 | 75
5 | 9 | 8.4 | 8.4 | 0.5 | 6 | 30 | 33 | 8 | 500 | 1 | 20 | 0.34052 | 2 | 0.02 | 10 | 40 | 2.5 | 75
Note on N10: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: 1

## Over Current
220 kV - Core 1
General parameters
Cable length | 90 | m
Cable cross-section | 4 | mm²
Maximum temperature | 75 | °C
CT secondary resistance Rct | 14 | Ohm
CT rated primary current Ipr | 2500 | A
CT rated secondary current Isr | 1 | A
IED input burden SR | 0.02 | VA
Accuracy limiting factor ALF | 20
Rated CT output Sn | 30 | VA
Intermediate calculations
Total secondary burden | 14.9777 | Ohm
Available CT Eal | 880 | V
REF650 Over Current Calculation
Inputs
The primary operate value | 1000 | A
Maximum close-in fault current | 31500 | A
Results
Criterion 1: Ealreq equation 336 | 352 | V
Criterion 2: Ealreq equation 337 | 554.4 | V
Required Eal | 554.4 | V
Pass / fail | pass
REF630 Over Current Calculation
Results
Actual burden of the current transformer | 0.97772 | VA
Approximate value of the accuracy limit factor | 58.7539
Reqierd ALF | 8
Pass / fail | pass

## 220 - 1
220 kV - Core 1
General parameters
Cable length | 90 | m
Cable cross-section | 4 | mm²
Maximum temperature | 75 | °C
CT secondary resistance Rct | 7 | Ohm
CT rated primary current Ipr | 800 | A
CT rated secondary current Isr | 1 | A
IED input burden SR | 0.02 | VA
Accuracy limiting factor ALF | 20
Rated CT output Sn | 30 | VA
Intermediate calculations
Total secondary burden | 7.9777 | Ohm
Available CT Eal | 740 | V
RET670 - CT Requirement for Transformer Differential Protection
Inputs
Transformer Rating St | 220 | MVA
Nominal system voltage | 220 | kV
Transformer impedance | 23 | %
Current bypassing the transformer If | 54654184 | A
Intermediate calculations
Transformer rated primary current Irt | 577.3503 | A
Max. current through two main CTs and transformer Itf | 2510.2186 | A
Results
Ealreq criterion 1: transformer rated current | 172.7227 | V
Ealreq criterion 2: through-fault current | 50.0645 | V
Required Eal | 172.7227 | V
Pass / fail | pass
RED670 - CT Requirement for Line Differential Protection
Inputs
Maximum internal close-in fault current Ikmax | 50000 | A
Maximum external through-fault current Itmax | 50000 | A
Results
Ealreq equation 601: internal close-in fault | 498.6074 | V
Ealreq equation 602: external through-fault | 997.2148 | V
Required Eal | 997.2148 | V
Pass / fail | fail

## 150 - 1
150 kV - Core 1
General parameters
Cable length | 65 | m
Cable cross-section | 4 | mm²
Maximum temperature | 75 | °C
CT secondary resistance Rct | 7 | Ohm
CT rated primary current Ipr | 1250 | A
CT rated secondary current Isr | 1 | A
IED input burden SR | 0.02 | VA
Accuracy limiting factor ALF | 20
Rated CT output Sn | 10 | VA
Intermediate calculations
Total secondary burden | 7.7117 | Ohm
Available CT Eal | 340 | V
RET670 - CT Requirement for Transformer Differential Protection
Inputs
Transformer Rating St | 310 | MVA
Nominal system voltage | 150 | kV
Transformer impedance | 18 | %
Current bypassing the transformer If | 6.6 | A
Intermediate calculations
Transformer rated primary current Irt | 1193.1906 | A
Max. current through two main CTs and transformer Itf | 6628.8364 | A
Results
Ealreq criterion 1: transformer rated current | 220.8362 | V
Ealreq criterion 2: through-fault current | 81.7912 | V
Required Eal | 220.8362 | V
Pass / fail | pass
RED670 - CT Requirement for Line Differential Protection
Inputs
Maximum internal close-in fault current Ikmax | 6600 | A
Maximum external through-fault current Itmax | 50000 | A
Results
Ealreq equation 601: internal close-in fault | 40.7177 | V
Ealreq equation 602: external through-fault | 616.9348 | V
Required Eal | 616.9348 | V
Pass / fail | fail

## 150 - 2
150 kV - Core 2
General parameters
Cable length | 65 | m
Cable cross-section | 4 | mm²
Maximum temperature | 75 | °C
CT secondary resistance Rct | 7 | Ohm
CT rated primary current Ipr | 1250 | A
CT rated secondary current Isr | 1 | A
IED input burden SR | 0.02 | VA
Accuracy limiting factor ALF | 20
Rated CT output Sn | 10 | VA
Intermediate calculations
Total secondary burden | 7.7117 | Ohm
Available CT Eal | 340 | V
RET670 - CT Requirement for Transformer Differential Protection
Inputs
Transformer Rating St | 325 | MVA
Nominal system voltage | 150 | kV
Transformer impedance | 5 | %
Current bypassing the transformer If | 29 | A
Intermediate calculations
Transformer rated primary current Irt | 1250.9256 | A
Max. current through two main CTs and transformer Itf | 25018.5117 | A
Results
Ealreq criterion 1: transformer rated current | 231.5219 | V
Ealreq criterion 2: through-fault current | 308.6958 | V
Required Eal | 308.6958 | V
Pass / fail | pass
RED670 - CT Requirement for Line Differential Protection
Inputs
Maximum internal close-in fault current Ikmax | 29000 | A
Maximum external through-fault current Itmax | 40000 | A
Results
Ealreq equation 601: internal close-in fault | 178.9111 | V
Ealreq equation 602: external through-fault | 493.5479 | V
Required Eal | 493.5479 | V
Pass / fail | fail

## 150 - 3
150 kV - Core 3
General parameters
Cable length | 75 | m
Cable cross-section | 4 | mm²
Maximum temperature | 75 | °C
CT secondary resistance Rct | 7.5 | Ohm
CT rated primary current Ipr | 1250 | A
CT rated secondary current Isr | 1 | A
IED input burden SR | 0.02 | VA
Accuracy limiting factor ALF | 20
Rated CT output Sn | 30 | VA
Intermediate calculations
Total secondary burden | 8.3181 | Ohm
Available CT Eal | 750 | V
RET670 - CT Requirement for Transformer Differential Protection
Inputs
Transformer Rating St | 310 | MVA
Nominal system voltage | 150 | kV
Transformer impedance | 18 | %
Current bypassing the transformer If | 8 | A
Intermediate calculations
Transformer rated primary current Irt | 1193.1906 | A
Max. current through two main CTs and transformer Itf | 6628.8364 | A
Results
Ealreq criterion 1: transformer rated current | 238.2018 | V
Ealreq criterion 2: through-fault current | 88.2229 | V
Required Eal | 238.2018 | V
Pass / fail | pass
RED670 - CT Requirement for Line Differential Protection
Inputs
Maximum internal close-in fault current Ikmax | 40000 | A
Maximum external through-fault current Itmax | 40000 | A
Results
Ealreq equation 601: internal close-in fault | 266.1791 | V
Ealreq equation 602: external through-fault | 532.3583 | V
Required Eal | 532.3583 | V
Pass / fail | pass

## 150 - 4
150 kV - Core 4
General parameters
Cable length | 70 | m
Cable cross-section | 4 | mm²
Maximum temperature | 75 | °C
CT secondary resistance Rct | 7.5 | Ohm
CT rated primary current Ipr | 1600 | A
CT rated secondary current Isr | 1 | A
IED input burden SR | 0.02 | VA
Accuracy limiting factor ALF | 40
Rated CT output Sn | 10 | VA
Intermediate calculations
Total secondary burden | 8.2649 | Ohm
Available CT Eal | 700 | V
RET670 - CT Requirement for Transformer Differential Protection
Inputs
Transformer Rating St | 200 | MVA
Nominal system voltage | 150 | kV
Transformer impedance | 15 | %
Current bypassing the transformer If | 6 | A
Intermediate calculations
Transformer rated primary current Irt | 769.8004 | A
Max. current through two main CTs and transformer Itf | 5132.0024 | A
Results
Ealreq criterion 1: transformer rated current | 119.2934 | V
Ealreq criterion 2: through-fault current | 53.0193 | V
Required Eal | 119.2934 | V
Pass / fail | pass
RED670 - CT Requirement for Line Differential Protection
Inputs
Maximum internal close-in fault current Ikmax | 40000 | A
Maximum external through-fault current Itmax | 40000 | A
Results
Ealreq equation 601: internal close-in fault | 206.6223 | V
Ealreq equation 602: external through-fault | 413.2446 | V
Required Eal | 413.2446 | V
Pass / fail | pass

## 33 - 1
33 kV - Core 1
General parameters
Cable length | 13 | m
Cable cross-section | 1.5 | mm²
Maximum temperature | 75 | °C
CT secondary resistance Rct | 14 | Ohm
CT rated primary current Ipr | 2500 | A
CT rated secondary current Isr | 1 | A
IED input burden SR | 0.02 | VA
Accuracy limiting factor ALF | 20
Rated CT output Sn | 15 | VA
Intermediate calculations
Total secondary burden | 14.3889 | Ohm
Available CT Eal | 580 | V
RET670 - CT Requirement for Transformer Differential Protection
Inputs
Transformer Rating St | 110 | MVA
Nominal system voltage | 33 | kV
Transformer impedance | 12 | %
Current bypassing the transformer If | 16 | A
Intermediate calculations
Transformer rated primary current Irt | 1924.5009 | A
Max. current through two main CTs and transformer Itf | 16037.5075 | A
Results
Ealreq criterion 1: transformer rated current | 332.2974 | V
Ealreq criterion 2: through-fault current | 184.6097 | V
Required Eal | 332.2974 | V
Pass / fail | pass
RED670 - CT Requirement for Line Differential Protection
Inputs
Maximum internal close-in fault current Ikmax | 31500 | A
Maximum external through-fault current Itmax | 31500 | A
Results
Ealreq equation 601: internal close-in fault | 181.3001 | V
Ealreq equation 602: external through-fault | 362.6003 | V
Required Eal | 362.6003 | V
Pass / fail | pass

## 33 - 2
33 kV - Core 2
General parameters
Cable length | 110 | m
Cable cross-section | 4 | mm²
Maximum temperature | 75 | °C
CT secondary resistance Rct | 20 | Ohm
CT rated primary current Ipr | 3000 | A
CT rated secondary current Isr | 1 | A
IED input burden SR | 0.02 | VA
Accuracy limiting factor ALF | 60
Rated CT output Sn | 30 | VA
Intermediate calculations
Total secondary burden | 21.1905 | Ohm
Available CT Eal | 3000 | V
RET670 - CT Requirement for Transformer Differential Protection
Inputs
Transformer Rating St | 175 | MVA
Nominal system voltage | 33 | kV
Transformer impedance | 12 | %
Current bypassing the transformer If | 29 | A
Intermediate calculations
Transformer rated primary current Irt | 3061.706 | A
Max. current through two main CTs and transformer Itf | 25514.2164 | A
Results
Ealreq criterion 1: transformer rated current | 648.7922 | V
Ealreq criterion 2: through-fault current | 360.4401 | V
Required Eal | 648.7922 | V
Pass / fail | pass
RED670 - CT Requirement for Line Differential Protection
Inputs
Maximum internal close-in fault current Ikmax | 40000 | A
Maximum external through-fault current Itmax | 40000 | A
Results
Ealreq equation 601: internal close-in fault | 282.5406 | V
Ealreq equation 602: external through-fault | 565.0812 | V
Required Eal | 565.0812 | V
Pass / fail | pass

## 33 - 3
33 kV - Core 3
General parameters
Cable length | 55 | m
Cable cross-section | 4 | mm²
Maximum temperature | 75 | °C
CT secondary resistance Rct | 14 | Ohm
CT rated primary current Ipr | 2500 | A
CT rated secondary current Isr | 1 | A
IED input burden SR | 0.02 | VA
Accuracy limiting factor ALF | 20
Rated CT output Sn | 20 | VA
Intermediate calculations
Total secondary burden | 14.6053 | Ohm
Available CT Eal | 680 | V
RET670 - CT Requirement for Transformer Differential Protection
Inputs
Transformer Rating St | 155 | MVA
Nominal system voltage | 33 | kV
Transformer impedance | 12 | %
Current bypassing the transformer If | 25 | A
Intermediate calculations
Transformer rated primary current Irt | 2711.7967 | A
Max. current through two main CTs and transformer Itf | 22598.306 | A
Results
Ealreq criterion 1: transformer rated current | 475.2784 | V
Ealreq criterion 2: through-fault current | 264.0435 | V
Required Eal | 475.2784 | V
Pass / fail | pass
RED670 - CT Requirement for Line Differential Protection
Inputs
Maximum internal close-in fault current Ikmax | 29000 | A
Maximum external through-fault current Itmax | 30000 | A
Results
Ealreq equation 601: internal close-in fault | 169.4212 | V
Ealreq equation 602: external through-fault | 350.5265 | V
Required Eal | 350.5265 | V
Pass / fail | pass

## 33 - 4
33 kV - Core 4
General parameters
Cable length | 80 | m
Cable cross-section | 4 | mm²
Maximum temperature | 75 | °C
CT secondary resistance Rct | 18 | Ohm
CT rated primary current Ipr | 3000 | A
CT rated secondary current Isr | 1 | A
IED input burden SR | 0.02 | VA
Accuracy limiting factor ALF | 20
Rated CT output Sn | 20 | VA
Intermediate calculations
Total secondary burden | 18.8713 | Ohm
Available CT Eal | 760 | V
RET670 - CT Requirement for Transformer Differential Protection
Inputs
Transformer Rating St | 155 | MVA
Nominal system voltage | 33 | kV
Transformer impedance | 10 | %
Current bypassing the transformer If | 25 | A
Intermediate calculations
Transformer rated primary current Irt | 2711.7967 | A
Max. current through two main CTs and transformer Itf | 27117.9672 | A
Results
Ealreq criterion 1: transformer rated current | 511.7514 | V
Ealreq criterion 2: through-fault current | 341.1676 | V
Required Eal | 511.7514 | V
Pass / fail | pass
RED670 - CT Requirement for Line Differential Protection
Inputs
Maximum internal close-in fault current Ikmax | 29000 | A
Maximum external through-fault current Itmax | 29000 | A
Results
Ealreq equation 601: internal close-in fault | 182.4226 | V
Ealreq equation 602: external through-fault | 364.8452 | V
Required Eal | 364.8452 | V
Pass / fail | pass

## 33 - 5
33 kV - Core 5
General parameters
Cable length | 40 | m
Cable cross-section | 2.5 | mm²
Maximum temperature | 75 | °C
CT secondary resistance Rct | 2 | Ohm
CT rated primary current Ipr | 500 | A
CT rated secondary current Isr | 1 | A
IED input burden SR | 0.02 | VA
Accuracy limiting factor ALF | 20
Rated CT output Sn | 10 | VA
Intermediate calculations
Total secondary burden | 2.701 | Ohm
Available CT Eal | 240 | V
RET670 - CT Requirement for Transformer Differential Protection
Inputs
Transformer Rating St | 30 | MVA
Nominal system voltage | 33 | kV
Transformer impedance | 8 | %
Current bypassing the transformer If | 6 | A
Intermediate calculations
Transformer rated primary current Irt | 524.8639 | A
Max. current through two main CTs and transformer Itf | 6560.7985 | A
Results
Ealreq criterion 1: transformer rated current | 85.0608 | V
Ealreq criterion 2: through-fault current | 70.884 | V
Required Eal | 85.0608 | V
Pass / fail | pass
RED670 - CT Requirement for Line Differential Protection
Inputs
Maximum internal close-in fault current Ikmax | 8400 | A
Maximum external through-fault current Itmax | 8400 | A
Results
Ealreq equation 601: internal close-in fault | 45.3775 | V
Ealreq equation 602: external through-fault | 90.7551 | V
Required Eal | 90.7551 | V
Pass / fail | pass

## Results
CT Calculation Results & SECP Comparison
Calculation sheet | Protection function | Excel criterion 1 (V) | Excel criterion 2 (V) | Excel proposed Eal (V) | Excel status | SECP criterion 1 (V) | SECP criterion 2 (V) | SECP proposed Eal (V) | SECP status | Spalte1 | Spalte 2 | Excel / SECP (%) | RL SECP (Ohm) | RL Error (%)
220 - 1 | Transformer differential | 172.7227 | 50.0645 | 740 | pass | 195.6871 | 56.7209 | 740 | pass | 13.2956 | 13.2956 | 88.26% | 1.0092 | 5.375%
220 - 1 | Line differential | 498.6074 | 997.2148 | 740 | fail | 501.825 | 1003.65 | 740 | fail | 0.64532 | 0.64532 | 99.36% | 1.0092 | 5.375%
150 - 1 | Transformer differential | 220.8362 | 81.7912 | 340 | pass | 242.7694 | 89.9146 | 340 | pass | 9.9319 | 9.9319 | 90.97% | 0.7288 | 5.366%
150 - 1 | Line differential | 40.7177 | 616.9348 | 340 | fail | 40.9137 | 619.904 | 340 | fail | 0.48137 | 0.48128 | 99.52% | 0.7288 | 5.366%
150 - 2 | Transformer differential | 231.5219 | 308.6958 | 340 | pass | 254.5163 | 339.3551 | 340 | pass | 9.9319 | 9.9319 | 90.97% | 0.7288 | 5.366%
150 - 2 | Line differential | 178.9111 | 493.5479 | 340 | fail | 179.7722 | 495.9232 | 340 | fail | 0.4813 | 0.48128 | 99.52% | 0.7288 | 5.366%
150 - 3 | Transformer differential | 238.2018 | 88.2229 | 750 | pass | 263.5138 | 97.5977 | 750 | pass | 10.6263 | 10.6263 | 90.39% | 0.841 | 5.375%
150 - 3 | Line differential | 266.1791 | 532.3583 | 750 | pass | 267.552 | 535.104 | 750 | pass | 0.51576 | 0.51576 | 99.49% | 0.841 | 5.375%
150 - 4 | Transformer differential | 119.2934 | 53.0193 | 700 | pass | 131.2 | 58.3111 | 700 | pass | 9.9809 | 9.9809 | 90.92% | 0.7849 | 5.371%
150 - 4 | Line differential | 206.6223 | 413.2446 | 700 | pass | 207.6225 | 415.245 | 700 | pass | 0.48407 | 0.48407 | 99.52% | 0.7849 | 5.371%
33 - 1 | Transformer differential | 332.2974 | 184.6097 | 580 | pass | 341.4496 | 189.6942 | 580 | pass | 2.7542 | 2.7542 | 97.32% | 0.3826 | 3.714%
33 - 1 | Line differential | 181.3001 | 362.6003 | 580 | pass | 181.4728 | 362.9455 | 580 | pass | 0.095242 | 0.095215 | 99.9% | 0.3826 | 3.714%
33 - 2 | Transformer differential | 648.7922 | 360.4401 | 3000 | pass | 688.4797 | 382.4887 | 3000 | pass | 6.1171 | 6.1171 | 94.24% | 1.2334 | 5.37%
33 - 2 | Line differential | 282.5406 | 565.0812 | 3000 | pass | 283.3787 | 566.7573 | 3000 | pass | 0.29663 | 0.29662 | 99.7% | 1.2334 | 5.37%
33 - 3 | Transformer differential | 475.2784 | 264.0435 | 680 | pass | 496.3694 | 275.7608 | 680 | pass | 4.4376 | 4.4376 | 95.75% | 0.6167 | 5.37%
33 - 3 | Line differential | 169.4212 | 350.5265 | 680 | pass | 169.7857 | 351.2808 | 680 | pass | 0.21517 | 0.21518 | 99.79% | 0.6167 | 5.37%
33 - 4 | Transformer differential | 511.7514 | 341.1676 | 760 | pass | 537.3154 | 358.2103 | 760 | pass | 4.9954 | 4.9954 | 95.24% | 0.897 | 5.368%
33 - 4 | Line differential | 182.4226 | 364.8452 | 760 | pass | 182.8643 | 365.7287 | 760 | pass | 0.24212 | 0.24215 | 99.76% | 0.897 | 5.368%
33 - 5 | Transformer differential | 85.0608 | 70.884 | 240 | pass | 109.0184 | 90.8487 | 240 | pass | 28.1652 | 28.1653 | 78.02% | 0.7209 | 5.852%
33 - 5 | Line differential | 45.3775 | 90.7551 | 240 | pass | 46.0471 | 92.0942 | 240 | pass | 1.4755 | 1.4755 | 98.55% | 0.7209 | 5.852%

## Entscheidungsmatrix
Decision Matrix – Transformer Differential Protection
Data-Driven Metrics
Number of transformer differential cases analyzed | 10
Minimum deviation between Excel and SECP | 2.68%
Average deviation between Excel and SECP | 8.791%
Maximum deviation between Excel and SECP | 21.98%
Pass/fail agreement | 100%
Direction of deviation | SECP higher than Excel
Weighted Quality Assessment
Category | Weight | Score (0–4) | Weighted Contribution | Example Rationale | Error Direction | Action | Status
Correctness of the calculation method | 20% | 3 | 15%
Safety impact of deviations | 20% | 4 | 20%
Numerical accuracy of the results | 20% | 2 | 10%
Documentation and presentation quality | 15% | 1 | 3.75%
Correctness of input processing | 10% | 3 | 7.5%
Consistency of the suitability decision | 10% | 4 | 10%
Traceability and reproducibility | 5% | 4 | 5%
Evaluated Weight | 100%
Normalized Overall Result | 71.25%
Decision Matrix – Line Differential Protection
Data-Driven Metrics
Number of line differential cases analyzed | 10
Minimum deviation between Excel and SECP | 0.09512%
Average deviation between Excel and SECP | 0.4895%
Maximum deviation between Excel and SECP | 1.454%
Pass/fail agreement | 100%
Direction of deviation | SECP higher than Excel
Weighted Quality Assessment
Category | Weight | Score (0–4) | Weighted Contribution | Example Rationale | Error Direction | Action | Status
Correctness of the calculation method | 20% | 4 | 20%
Safety impact of deviations | 20% | 4 | 20%
Numerical accuracy of the results | 20% | 3 | 15%
Documentation and presentation quality | 15% | 1 | 3.75%
Correctness of input processing | 10% | 3 | 7.5%
Consistency of the suitability decision | 10% | 4 | 10%
Traceability and reproducibility | 5% | 4 | 5%
Evaluated Weight | 100%
Normalized Overall Result | 81.25%
Data Basis – Transformer Differential Protection
Calculation Sheet | Excel Criterion 1 [V] | Excel Criterion 2 [V] | SECP Criterion 1 [V] | SECP Criterion 2 [V] | Deviation of Governing Criterion | Excel Status | SECP Status
220 - 1 | 172.7227 | 50.0645 | 195.6871 | 56.7209 | 11.74% | pass | pass
150 - 1 | 220.8362 | 81.7912 | 242.7694 | 89.9146 | 9.035% | pass | pass
150 - 2 | 231.5219 | 308.6958 | 254.5163 | 339.3551 | 9.035% | pass | pass
150 - 3 | 238.2018 | 88.2229 | 263.5138 | 97.5977 | 9.606% | pass | pass
150 - 4 | 119.2934 | 53.0193 | 131.2 | 58.3111 | 9.075% | pass | pass
33 - 1 | 332.2974 | 184.6097 | 341.4496 | 189.6942 | 2.68% | pass | pass
33 - 2 | 648.7922 | 360.4401 | 688.4797 | 382.4887 | 5.765% | pass | pass
33 - 3 | 475.2784 | 264.0435 | 496.3694 | 275.7608 | 4.249% | pass | pass
33 - 4 | 511.7514 | 341.1676 | 537.3154 | 358.2103 | 4.758% | pass | pass
33 - 5 | 85.0608 | 70.884 | 109.0184 | 90.8487 | 21.98% | pass | pass
Data Basis – Line Differential Protection
Calculation Sheet | Excel Criterion 1 [V] | Excel Criterion 2 [V] | SECP Criterion 1 [V] | SECP Criterion 2 [V] | Deviation of Governing Criterion | Excel Status | SECP Status
220 - 1 | 498.6074 | 997.2148 | 501.825 | 1003.65 | 0.6412% | fail | fail
150 - 1 | 40.7177 | 616.9348 | 40.9137 | 619.904 | 0.479% | fail | fail
150 - 2 | 178.9111 | 493.5479 | 179.7722 | 495.9232 | 0.479% | fail | fail
150 - 3 | 266.1791 | 532.3583 | 267.552 | 535.104 | 0.5131% | pass | pass
150 - 4 | 206.6223 | 413.2446 | 207.6225 | 415.245 | 0.4817% | pass | pass
33 - 1 | 181.3001 | 362.6003 | 181.4728 | 362.9455 | 0.09512% | pass | pass
33 - 2 | 282.5406 | 565.0812 | 283.3787 | 566.7573 | 0.2957% | pass | pass
33 - 3 | 169.4212 | 350.5265 | 169.7857 | 351.2808 | 0.2147% | pass | pass
33 - 4 | 182.4226 | 364.8452 | 182.8643 | 365.7287 | 0.2416% | pass | pass
33 - 5 | 45.3775 | 90.7551 | 46.0471 | 92.0942 | 1.454% | pass | pass